�,!.la�ENGlt-flRS

��W'N::>IA LIMITED

l.fflm'�ffll'J:RIA'II	(A.Go..t.aflndiaUndertak1ng)

FOR HAZARDOUS AREA LIGHT FIXTURES AND JUNCTION

6-51-0061 Rev. 6

Page 1 of 8

BOXES

•

�II�f211	Nicf fl-q�]

# �ct;el

�  �	fctH��I

SPECIFICATION FOR

HAZARDOUS AREA LIGHT FIXTURES

AND JUNCTION BOXES

| 6 | 23.12.20 |
| --- | --- |
| 5 | 24.02.16 |
| 4 | 11.04.11 |
| 3 | 27.08.07 |
| 2 | 30.01.02 |

REVISED AND ISSUED AS STANDARD SPECIFICATION

REVISED AND ISSUED AS STANDARD	NNB/AK	ANPS	BRB	SC SPECIFICATION

REVISED AND ISSUED AS STANDARD	PS	ANPS	UAP	DM SPECIFICATION

vc

REVISED AND ISSUED AS STANDARD	ANPS	UAP	JMS SPECIFICATION

REVISED AND ISSUED AS STANDARD	UAP	AAN	VPS	GRR SPECIFICATION

Rev.

Date	Purpose

Standards	Standards

Prepared	Checked	Committee	Bureau

No	,	by	by

Convenor	Chairman Approved by

Abbreviations:

AC BIS CEA CRI DC DGCA EIL FRLS IEC IES

IP IS LED MR

NABL PESO PO PVC SPD SPN

ss

XLPE

Alternating Current

Bureau of Indian Standards Central Electricity Authority Colour Rendering Index Direct Current

Director General Civil Aviation Engineers India Limited

Flame Retardant Low Smoke

International Electrotechnical Commission Illuminating Engineering Society

Ingress Protection Indian Standard Light Emitting Diode Material Requisition

National Accreditation Board for Testing and Calibration Laboratories Petroleum and Explosives Safety Organisation

Purchase Order Poly Vinyl Chloride

Surge Protection Device Single Phase Neutral Stainless Steel

Cross Linked Poly Ethylene

Electrical Standards Committee

Convenor: Members:

Mr. Parag Gupta

Mr. M. K. Sahu

Ms. Arvind N. P. Singh Mr. Harish Kumar

Ms. Shalini Verma Mr. Raman Sood Mr. V. K. Jain

Ms. Shirali Aggarwal

Mr. Ayush Mathur (Projects) Mr. Rajesh Sinha (Inspection)

FOR HAZARDOUS AREA LIGHT FIXTURES AND JUNCTION

6-51-0061 Rev. 6

Page 3 of 8

BOXES

CONTENTS

- SCOPE	4

- CODES AND STANDARDS	4

- GENERAL REQUIREMENTS	4

- SITE CONDITIONS	4

- POWER SUPPLY	5

- CERTIFICATION/	5

- TECIINICAL REQUIREMENTS	5

- INSPECTION, TESTING AND ACCEPTANCE	7

- PACKING AND DESPATCH	7

�2ld·8'0N:ERS

�	�WINDIA LIMITED

C��ll"ll�l	IAGcM.oitndiaUl'ldertlklng)

FOR HAZARDOUS AREA LIGHT FIXTURES AND JUNCTION

6-51-0061 Rev. 6

Page 4 of 8

BOXES

# SCOPE

This specification covers the requirements of design, manufacture, testing, packing and supply of LED lighting fixtures, complete with LED lamp and driver, junction boxes and accessories suitable for installation in locations handling flammable liquids and gases/ vapours.

# CODES AND STANDARDS

  - The equipment shall comply with the requirements of latest revision of the following standards issued by BIS:

IS-5

IS-10322 IS-13383

IS 15885 (Part 2/

Sec 13) IS-16101

IS-16102 TS-16107

IS / IEC 60079-0 IS / IEC 60079-1 IS/ IEC 60079-7

IS/ IEC 60079-15 IS / IEC 60529

Colours for ready mixed paints and enamels Luminaires

Photometry of luminaires - Method of measurement

Safety of lamp control gear-Part-2 Particular requirements-Section 13 d.c. or a.c. supplied electronic control gear for LED modules General lighting- LEDs and LED modules-Terms and

Definitions

Self-ballasted LED lamps for general lighting services Luminaires performance

Electrical apparatus for explosive gas atmospheres (General requirements)

Electrical apparatus for explosive gas atmospheres (Equipment Protection by Flameproof Enclosures "d")

Electrical apparatus for explosive gas atmospheres (Equipment Protection by Increased Safety "e")

Electrical apparatus for explosive gas atmospheres Construction, test & marking of type of protection "n"

Degrees of protection provided by enclosures (IP Code).

  - In case of imported equipment, only IECEx (or equivalent, if more stringent than the applicable IEC) certified equipment shall be used.

  - The equipment shall also confirm to the provisions of CEA Regulations with latest amendments and statutory regulations currently in force in the country.

  - ln case Indian standards are not available for any equipment, standards issued by IEC or equivalent agency (if more stringent than IEC) shall be applicable.

  - In case of any conflict between requirements specified in various applicable documents for the project, the most stringent requirement shall govern. However, Owner's/ EIL's decision in this regard will be final and binding.

# GENERAL REQUIREMENTS

  - The offered equipment shall be brand new with state of art technology and having proven field track record. No prototype equipment shall be offered.

  - Vendor shall ensure availability of spare parts and maintenance support services for the offered equipment for at least 10 years from the date of supply.

# SITE CONDITIONS

The equipment shall be suitable for installation and satisfactory operation in classified hazardous locations in tropical, humid and corrosive atmosphere as prevalent in refineries,

Format No. 8-00-0001-F1 Rev. 0	Copyright Ell -All rights reseNed

�a	 �ENGll'EERS

��W'NDIALMTED

lfflii?'T�'-�1	!'4.Go-11 Oflf'ldiaUlldmMingJ

SPECIFICATION FOR

HAZARDOUS AREA LIGHT FIXTURES AND JUNCTION BOXES

STANDARD SPECIFICATION No.

6-51-0061 Rev. 6

Page 5of 8

petrochemical and fertilizer plants. Unless otherwise specified, a design ambient temperature of 40° C and an altitude not exceeding 1000 m above mean sea level shall be considered.

# POWER SUPPLY

All AC lighting fixtures/ junction boxes shall be suitable for 240V ± 10%, SPN, 50Hz ± 3% power supply and all DC lighting fixtures/ junction boxes shall be suitable for 110/ 220V ± 10% power supply.

# CERTIFICATION

The equipment shall have test certificates issued by NABL-approved/ Central Government labs in India/ TECEx-approved/ equivalent labs. All equipment (indigenous & imported) shall also have valid statutory approvals, as applicable, for the specified location, and marking as per IS/IEC 60079 and as required by statutory authorities. All indigenous flameproof equipment shall have valid BIS license.

- TECHNICAL REQUIREMENTS

  - Construction

    - The enclosures of the lighting fixtures and junction boxes shall be of cast light metal alloy.

    - All equipment shall be suitable for use in outdoor open locations and shall have minimum IP-55 degree of protection.

    - The enclosures shall be provided with gaskets made of non-inflammable and self-extinguishing material.

    - All metal surfaces shall undergo manufacturer's standard cleaning/ painting/ powder coating cycle. After surface preparation, the equipment shall be painted with two coats of epoxy based final paint or epoxy powder coated with minimum coating thickness of 80 microns, with colour shade as below:

      - FlameproofExd (Gas group HA/118) and AC supply: Dark admiralty grey shade 632 of lS-

5/ RAL 7031

      - Flameproof Exd (Gas group IIC) and AC Supply  : Light yellow shade 355 ofIS-5/ RAL

1012

      - Non-sparking ExnR/ Increased safety Exec and AC Supply

      - DC lighting fixtures

: Dark admiralty grey shade 632 of 1S-5/ RAL 7031

: Bright red shade 538 oflS-5/ RAL 3003

All unpainted parts shall be suitably treated to prevent rust formation/ corrosion. If these parts are moving elements then these shall be greased with non-solidifying grease.

    - A warning inscription "DO NOT OPEN WHEN ENERGIZED" shall be provided on each enclosure. The warning inscription shall be embossed on the enclosure or a separate warning plate with above inscription shall be fixed to the enclosure with screws. The warning plate shall be of nickel plated brass or stainless steel.

    - All accessories like nuts, bolts, washers etc. shall be made of stainless steel SS-304.

    - All equipments on single phase supply shall be provided with an independent earth terminal with lug inside the enclosure for terminating the third (earth) core of the cable and shall have facility for looping.

    - A nameplate shall be provided to indicate the details of testing agency, name of manufacturer, test certificate number, statutory approval agency (PESO), serial number, BIS license number, applicable gas group etc. and any additional marking required by statutory authority like approval no. etc. The nameplates shall be Al anodized or SS-304 engraved type or laser-

�a	�ENGII\EERS

�	™csWINDIA LIMITED

C��a,i�)	(AGcM.oftnaiaUndertaklng)

SPECIFICATION FOR

HAZARDOUS AREA LIGHT FIXTURES AND JUNCTION

STANDARD SPECIFICATION No.

6-51-0061 Rev. 6

Page 6 of 8

BOXES

marked and permanently fixed/ fixed with rivets on the equipment. In case the standard details given above are embossed on the enclosures, the same need not be repeated on the name plate.

  - Lighting Fixtures

7.2. l Glass used for all types of lighting fixtures shall be clear and suitable for use under conditions involving exceptional risk of mechanical damage. Glass shall be toughened type.

    - All well/ bowl glass fixtures shall be provided with Stainless Steel SS-304 protective wire cage using minimum 5mm welded steel construction and having mesh dimension not exceeding 50mm x 50 mm. The mounting bolts of SS-304 required for physically connecting the hazardous area well/ bowl glass lighting fixtures (bracket/ ceiling mounted type) to the respective mounting bracket shall be supplied by Vendor along with the fixtures.

    - The fixing parts of the enclosure, which are to be opened for replacement of lamp, shall be so fastened that they can be unfastened only with special tools.

    - The lighting fixtures in Zone-2 area shall be Ex nR type, unless otherwise specified in the MR/ Tender.

    - For LED fixture, integral junction box shall be provided with 3 nos. cable entries for loop-in, loop-out and associated wiring to fixture. Alternatively, lighting fixtures shall be provided with 2 nos. threaded entries and 2 nos. hazardous area double compression nickel plated brass cable glands, and internal wiring shall be provided for driver and lamp. The glands shall be suitable for the specified cable size. 20% of the fixtures shall be supplied with l no. nickel plated brass plug for sealing the unused entry.

    - The top of all well/ bowl glass lighting fixtures shall be identically drilled/ threaded to facilitate installation on pole/ column or ceiling.

    - The flood lighting fixtures shall be supplied with adjustable mounting arrangement both in horizontal and vertical plane.

    - The aviation warning lighting fixtures shall have cluster LED lamps of Type C, medium intensity (as per DGCA civil aviation statutory regulations) and of red colour, fixed (not flashing), 2000cd, unless otherwise specified.

    - All lighting fixtures shall be provided with suitable mirror-polished aluminum internal reflector of suitable thickness to ensure adequate mechanical strength.

    - Lighting fixtures shall be tested for resistance to impact in line with IS/ IEC 60079-0. Impact test certificates shall be furnished by vendor.

    - All LED fixtures shall be supplied complete with lamp and driver. LED driver shall be suitable for surge protection of minimum 4 kV surge. However, for flood lights, aviation warning lights, and lighting fixtures with wattage higher than 90W, LED driver shall be suitable for surge protection of minimum 10 kV surge. An additional fail safe SPD may be provided, as required, to achieve 10 kV surge protection. LED driver shall comply with the requirement of IS 15885-2-13. Fixture lifetime (L70) shall be greater than 50000 hours at ambient temperature of 40°C.

    - LED type lighting fixtures shall fulfill the following requirements:

      - Minimum power factor shall be 0.95.

      - LED lighting fixture luminous efficacy shall be minimum 100 lumen per watt.

      - LED lighting fixture beam angle shall be 120°/ 90' depending upon fixture location and mounting height.

      - The CRI for LED lighting fixtures shall be greater than 80 for indoor fixture and greater than 70 for outdoor fixture.

SPECIFICATION FOR

HAZARDOUS AREA LIGHT FIXTURES AND JUNCTION

STANDARD SPECIFICATION No.

6-51-0061 Rev. 6

Page 7 of 8

BOXES

      - The colour temperature of white colour LED shall be from 5700K to 6500K, unless otherwise specified.

      - Polar curves/ photometric drawings shall be submitted by vendor for the offered lighting fixtures.

      - LED lamps and drivers shall be provided with minimum 5 years warranty period, unless specified otherwise in the MR/ Tender. Driver shall have valid BIS certification and the same shall be furnished during drawing review stage.

      - The LED light fixtures, should be tested for luminous lux level as per IES-LM-79. Wherever wire guard is provided, testing shall be done with wire guard. Type test certificates for LM-79 for all fixtures shall be from an NABL-accredited/ IECEx-certified/ equivalent lab.

      - The LEDs used in the lighting fixtures should be tested for the service life as per IES-LM-80. Type test certificates shall be furnished in compliance to same.

  - Junction Boxes

The junction boxes shall be of flameproof or non-sparking type construction as mentioned in the MR/ Datasheet. All junction boxes for looping of single phase lighting circuits using cables up to 6mm2 shall be minimum 125mm diameter in size. Each junction box shall be complete with requisite number of cable entries and double compression flameproof nickel plated brass cable glands to suit the specified cable size.

  - Terminals & Wiring

    - The fixtures and junction boxes shall be provided with sufficient number of terminals. More than 2 wires per terminal shall not be permitted. If required, additional terminal with shorting link may be used. The terminals for external cable termination shall be suitable for 2.5mm2 solid Copper conductor. Tinned copper lugs shall be provided for cable termination wherever applicable.

    - All internal wiring shall employ l.5mm2, 660/ ll00 V grade, FRLS type, XLPE/ PVC insulated Copper conductor wires, colour coded for phase, neutral and earth. All termination shall be with suitable lugs.

# INSPECTION, TESTING AND ACCEPTANCE

  - During fabrication, the equipment shall be subjected to inspection by EIL/ Owner or by an agency authorised by the Owner, as per agreed Inspection Test Plan. Manufacturer shall furnish all necessary information concerning the supply to EIL/ Owner's inspector. All routine/ acceptance tests shall be carried out at manufacturer's works under his care and expense.

  - Type test certificates from NABL-approved/ Central Government Labs in India/ IECEx-certified/ equivalent Labs, Manufacturer's works test reports, applicable PESO approval and BIS license shall be shown to the inspection agency on demand during inspection. The certificates, BIS license and PESO approval must be valid at the time of despatch.

  - Test certificates of bought out components shall be submitted to the inspection agency, as per Inspection and Test Plan no. 6-81-1061.

  - All equipments shall be subjected to various routine/ acceptance tests as per Inspection and Test Plan no. 6-81-1061.

# PACKING AND DESPATCH

All the equipment shall be divided into several sections for protection and ease of handling during transportation. The equipment shall be properly packed for the selected mode of transportation, i.e. by ship/ rail or trailer, and shall be wrapped in polythene sheets before

��a  �ENGII\EERS

�	�W'INDIA LIMITED

(�  �Q!l'�J	fA GCNt.d India Undertaking)

SPECIFICATION FOR

HAZARDOUS AREA LIGHT FIXTURES AND JUNCTION

STANDARD SPECIFICATION No.

6-51-0061 Rev. 6

Page 8 of 8

BOXES

being placed in crates/ cases to prevent damage to finish. The crates/ cases shall have skid bottom for handling. Special notations such as 'Fragile', 'This side up', 'Center of gravity', 'Weight',' Owner's particulars', 'PO nos.' etc., shall be clearly marked on the packages together with other details as per purchase order.

The equipment may be stored outdoors for long periods before installation. The packing should be suitable for outdoor storage in areas with heavy rains and high ambient temperature unless otherwise agreed. A set of instruction manuals for installation, testing and commissioning, a set of operation & maintenance manuals and a set of final drawing shall be enclosed in a waterproof cover along with the shipment.